SHEPA PROJECT

HOMER Pro – Data Import Reference Document

Central Hub & Borehole System  |  Version 1.0

1. Purpose of This Document

This document provides all energy load data, design parameters, and system assumptions required to import and configure the Shepa Project in HOMER Pro. It is structured to match HOMER Pro's input categories, allowing direct entry of values during system modelling.

Two separate HOMER Pro models are required:

- Model A – Central Hub (cold storage, hydrogen production, water treatment, controls)

- Model B – Borehole System (one independent model per borehole; replicate 5 times)

2. Central Hub – Load Data for HOMER Pro

2.1  Equipment Load Table

Enter each row below as a load component in HOMER Pro. Categorise loads as AC Primary Load or Deferrable Load as indicated.

| Equipment / Load Name | Peak Power (kW) | Energy (kWh/day) | Operation Type | Hours/Day | HOMER Load Category |
| --- | --- | --- | --- | --- | --- |
| Cold Room HVAC (Compressors) | 8.5 | 204 | 24-Hour | 24 | AC Primary Load |
| Cold Room Fans & Controls | 1.5 | 36 | 24-Hour | 24 | AC Primary Load |
| Cold Room Lighting | 0.5 | 12 | 24-Hour | 24 | AC Primary Load |
| Control Room (SCADA, IT, Comms) | 0.8 | 19.2 | 24-Hour | 24 | AC Primary Load |
| Hydrogen Auxiliary Systems | 1.0 | 24 | 24-Hour | 24 | AC Primary Load |
| Electrolyzer | 30.0 | 240 | Daytime Only | 8 | Deferrable / AC Primary |
| Hydrogen Compressor | 4.0 | 16 | Daytime Only | 4 | Deferrable Load |
| Reverse Osmosis (RO) System | 0.1 | 0.8 | Daytime Only | 8 | Deferrable Load |
| Atm. Water Generator (AWG)* | 1.2 | 28.8 | Seasonal (Rainy) | 24 | AC Primary (seasonal) |

* AWG (Atmospheric Water Generator): include only in the Rainy Season scenario model. Exclude from the Dry Season model.

2.2  Central Hub Daily Energy Summary

Use these totals to verify your HOMER load profile after entry. Apply inverter (95%) and battery (85%) loss factors as shown.

| Season | Raw Energy (kWh/day) | Adjusted (with losses) kWh/day |
| --- | --- | --- |
| Dry Season (No AWG) | ~504 | ~550–600 |
| Rainy Season (With AWG) | ~533 | ~580–630 |

2.3  Non-Electrical Components (Include in System Diagram – No kW Load)

The following items must appear in the HOMER system diagram or notes but do not contribute electrical load:

- Hydrogen storage tanks – 10 to 20 kg capacity

- Hydrogen and water piping and valves

- Water storage tank – 200 to 500 L

- Cold room structural insulation panels

- Electrical distribution panels

- Safety systems: pressure relief valves, fire suppression

3. Borehole System – Load Data for HOMER Pro (Per Borehole)

3.1  Borehole Equipment Load Table

Model one borehole first. Duplicate the HOMER file four times for the remaining boreholes (5 total). Each borehole is an independent DC-coupled or AC-coupled solar pumping system with no battery storage assumed.

| Equipment / Load Name | Peak Power (kW) | Energy (kWh/day) | Operation Type | Hours/Day | HOMER Category |
| --- | --- | --- | --- | --- | --- |
| Submersible Water Pump | 5.0 | 25 | Daytime Only | 5 | Deferrable Load |
| Pump Controller (VFD) | 0.2 | 1.0 | Daytime Only | 5 | Deferrable Load |
| Borehole Monitoring Sensors | 0.05 | 1.2 | 24-Hour | 24 | AC Primary Load |

3.2  Per-Borehole Energy Total

- Total energy per borehole: approximately 27 kWh/day

- Total energy for all 5 boreholes: approximately 135 kWh/day

- Note: Do not combine borehole loads into the Central Hub HOMER model

4. Key Design Parameters for HOMER Pro Input

Enter the following values in the corresponding HOMER Pro input fields. These parameters are critical for accurate system sizing and optimisation.

| Parameter | Value | HOMER Input Location |
| --- | --- | --- |
| Solar Peak Hours (PSH) | 5.5 hrs/day | Solar Resource → Location / GHI data |
| Battery Round-Trip Efficiency | 85% | Storage → Battery Bank → Efficiency |
| Inverter Efficiency | 95% | Converter → Efficiency setting |
| Hydrogen Production Target | ~5 kg/day | Electrolyzer component sizing |
| Total Daily Head (TDH) | ~100 m | Pump load / deferrable load sizing |
| Battery Night Storage Requirement | ~180–200 kWh | Battery capacity (storage) setting |
| 24-Hour Critical Loads (Hub) | ~295 kWh/day | AC Primary Load profile |
| Daytime Operational Loads (Hub) | ~257 kWh/day | Deferrable Load / AC primary (daytime) |

5. Total System Energy Summary

Use this table to cross-check your HOMER model outputs against expected project-level totals.

| System / Sub-System | Energy (kWh/day) | Key Note |
| --- | --- | --- |
| Central Hub (Dry Season) | 550–600 | Exclude AWG in HOMER dry season model |
| Central Hub (Rainy Season) | 580–630 | Include AWG as seasonal load |
| Borehole System (per borehole) | ~27 | Model independently in separate HOMER file |
| 5 Boreholes (total) | ~135 | Sum of all 5 independent systems |
| Grand Total (Dry Season) | ~685–735 | Central Hub + all 5 Boreholes |

6. Critical Modelling Notes

- The hydrogen system (electrolyzer + compressor) accounts for approximately 50% of total hub energy. Ensure it is correctly categorised as a deferrable or primary load based on your dispatch strategy.

- Battery storage must be sized for night-time critical loads: target 180 to 200 kWh usable capacity. Apply second-life battery efficiency of 85% when sizing.

- Model dry season and rainy season as two separate HOMER scenarios to capture AWG impact.

- Borehole systems must be modelled independently – do not aggregate into the central hub model.

- Use the solar resource location data for Shepa to set GHI / PSH = 5.5 hours per day in the HOMER solar resource input.

- Set inverter efficiency to 95% in the converter settings.

7. Recommended HOMER Pro Model Structure

- homer_shepa_central_hub_dry.homer – Central Hub, Dry Season (no AWG)

- homer_shepa_central_hub_rainy.homer – Central Hub, Rainy Season (with AWG)

- homer_shepa_borehole_single.homer – Single Borehole Reference Model

- Duplicate borehole file x4 for remaining 4 boreholes as required

Shepa Project  |  HOMER Pro Data Import Reference  |  Prepared for HOMER Pro Design Phase